## Table 1
TD9
®
EPA Certified / Stationary Emergency
OUTPUT POWER OPTIONS | [12 empty] | 125°C RISE STANDBY RATING |  | 105°C RISE CONTINUOUS RATING |  |  |  | sKVA
Make | Voltage | Alternator | [5 empty] | Phase |  |  | Hertz |  | kW/kVA | Amps | kW/kVA |  |  | Amps | 30% Voltage Dip
Marathon | 600 | 281PSL5246 | [5 empty] | 3 |  |  | 60 |  | 9/11 | 11 | 8/10 |  |  | 10 | 33
| 277/480 | 281CSL1502 | [5 empty] | 3 |  |  | 60 |  | 9/11 | 14 | 8/10 |  |  | 12 | 30
| 120/208 | 281CSL1502 | [5 empty] | 3 |  |  | 60 |  | 9/11 | 31 | 8/10 |  |  | 28 | 23
| 120/240 | 281CSL1502 | [5 empty] | 3 |  |  | 60 |  | 9/11 | 27 | 8/10 |  |  | 24 | 23
| 120/240 | 281CSL1502 | [5 empty] | 1 |  |  | 60 |  | 8/8 | 33 | 7/7 |  |  | 29 | 9
| 120/240 | 281CSL1513 | [5 empty] | 1 |  |  | 60 |  | 9/9 | 38 | 8/8 |  |  | 33 | 11
Marathon | 277/480 | 282CSL1504 | [5 empty] | 3 |  |  | 60 |  | 10/13 | 15 | 9/11 |  |  | 14 | 48
| 120/208 | 282CSL1504 | [5 empty] | 3 |  |  | 60 |  | 10/13 | 35 | 9/11 |  |  | 31 | 36
| 120/240 | 282CSL1504 | [5 empty] | 3 |  |  | 60 |  | 10/13 | 30 | 9/11 |  |  | 27 | 36
| 120/240 | 282CSL1504 | [5 empty] | 1 |  |  | 60 |  | 9/9 | 38 | 8/8 |  |  | 33 | 18
Stamford | 600 | PI044F17 | [5 empty] | 3 |  |  | 60 |  | 9/11 | 11 | 8/10 |  |  | 10 | 39
| 277/480 | PI044F311 | [5 empty] | 3 |  |  | 60 |  | 9/11 | 14 | 8/10 |  |  | 12 | 35
| 120/208 | PI044F311 | [5 empty] | 3 |  |  | 60 |  | 9/11 | 31 | 8/10 |  |  | 28 | 26
| 120/240 | PI044F311 | [5 empty] | 3 |  |  | 60 |  | 9/11 | 27 | 8/10 |  |  | 24 | 26
| 120/240 | PI044F311 | [5 empty] | 1 |  |  | 60 |  | 9/9 | 38 | 8/8 |  |  | 33 | 19
947 Industrial Park Drive • Clinton, MS 39056 • Phone (601) 922-4444 • Fax (601) 922-0800 • www.taylorpower.com
application and engineering data
® Engine Data | [12 empty] | Air Requirements
Manufacturer |  |  |  | Perkins
Model |  |  |  | 403D-11G
Aspiration |  |  |  | Naturally Aspirated
EPA Tier |  |  |  | 4i
Arrangement |  |  |  | Vertical Inline, 4-Cycle
Firing Order |  |  |  | 1-2-3
Displacement: L (in.³) |  |  |  | 1.13 (69.02)
Bore: mm (in.) |  |  |  | 77.00 (3.03)
Stroke: mm (in.) |  |  |  | 81.00 (3.19)
Compression Ratio |  |  |  | 23:1
BMEP: psi (kPa) |  |  |  | N/A
Net Horsepower |  |  |  | 15.28
Rated RPM |  |  |  | 1800
Governor |  |  |  | Isochronous
Speed Regulation |  |  |  | ±0.75%
Air Filter(s) Type | [8 empty] | Dry
Combustion Air Flow: CFM (m³/min) | [8 empty] | 31.78 (0.90)
Maximum Air Intake Restriction
Clean: in. H2O (kPa) | [8 empty] | 12.04 (3.00)
Dirty: in. H2O (kPa) | [8 empty] | 25.69 (6.40)
Exhaust System
Gas Temperature: °F (°C) | [9 empty] | 959.0 (515.0)
Gas Flow: CFM (m³/min) | [9 empty] | 84.76 (2.40)
Max Exhaust Back Pressure: in. H2O (kPa) | [9 empty] | 40.94 (10.20)
Exhaust Outlet Size: in. (mm) | [9 empty] | 1.34 (34.00)
Sound Level
Open Unit Without Exhaust: dBA 3.2 ft (1M) 78.5
Filters and Quantity
Air Cleaner Quantity | [7 empty] | 1
Oil Filter(s) Quantity | [7 empty] | 1
Fuel Filter(s) Quantity | [7 empty] | 2
Engine Liquid Capacity
Oil System: qt. (L) 5.18 (4.90)
Cooling System Capacity: gal (L) 1.37 (5.20)
Fuel Consumption - 125°C Engine Electrical
At 100% of Power Rating: gal/hr (L/hr) | [9 empty] | 0.69 (2.63)
At 75% of Power Rating: gal/hr (L/hr) | [9 empty] | 0.54 (2.04)
At 50% of Power Rating: gal/hr (L/hr) | [9 empty] | 0.39 (1.48)
At 25% of Power Rating: gal/hr (L/hr) | [9 empty] | N/A
Electric Volts: DC |  |  |  |  | 12
Cold Cracking Amps |  |  |  |  | 525
Battery(s) Required |  |  |  |  | 1
Fuel System | [11 empty] | Fuel Consumption - 105°C
At 100% of Power Rating: gal/hr (L/hr) | [10 empty] | N/A
At 75% of Power Rating: gal/hr (L/hr) | [10 empty] | N/A
At 50% of Power Rating: gal/hr (L/hr) | [10 empty] | N/A
At 25% of Power Rating: gal/hr (L/hr) | [10 empty] | N/A
Fuel Injection Type | [5 empty] | Indirect
Fuel Pump Rate: gal/hr (L/hr) | [5 empty] | 998.57 (3780.00)
Pump Pressure: in. H2O (kPa) | [5 empty] | 50.00 (10.00)
Max Suction Head: ft (m) | [5 empty] | 2.63 (0.80)
Pump Max Pressure Head: ft (m) | [5 empty] | 9.84 (3.00)
Recommended Fuel | [5 empty] | Ultra Low Sulfur Diesel
Cooling System
Heat Rejection to Radiation: kW (BTUM) | [9 empty] | 3.10 (176.29)
Rejection to Coolant & Oil: kW (BTUM) | [9 empty] | 12.1 (688.1)
Coolant Flow: gal/min (L/min) | [9 empty] | 8.59 (32.50)
GENERAL GUIDELINES FOR DERATION: Altitude: Derate 0.5% per 100m (328 ft.) Elevation above 1000m (3279 ft.) Temperature: Derate 1.0% per 10°C (18°F) temperature above 25°C (77°F) RATINGS: All three-phase units are rated at 0.8 power factor. All single-phase units are rated at 1.0 power factor. 125° RATINGS: 125° apply to installations served by a reliable utility source. The standby rating is applicable to varying loads for the duration of a power outage. There is no overload capability for this rating. Ratings are in accordance with ISO-3046/1, BS 5514, AS 2789, and DIN 6271. 105° RATINGS: 105° ratings apply to installations where utility power in unavailable or unreliable. At varying load the number of generator set operating hours is unlimited. A 10% overload capacity is available for one hour in twelve. Ratings are in accordance with ISO-8528/1, overload power in accordance with ISO-3046/1, BS5514, AS2789, and DIN 6271. For limited running time and base load ratings consult the factory. The generator set manufacturer reserves the right to change the design or specifications without notice and without any obligation or liability whatsoever.
alternator and controller data
® Alternator Data Features
Manufacturer Marathon
Type Self-Excited
Insulation NEMA Rise/Temp NEMA H/125°C
Hertz 60
Phase 3
RPM 1800
Leads 12
Amortisseur Windings Full
CFM Cooling Required 250
Voltage Regulator SE350
Sensing Single Phase
Voltage Regulation, No Load - Full Load 1.0%
● NEMA MG1-32, BS5000, and IEC 34-1 compliant; CE & CSA Certified and UL Listed ● Self-ventilated and drip proof construction ● Two-thirds pitch stator and skewed rotor ● Wet wound, epoxied field windings ● Designed to withstand overspeeds of up to 125% ● Analog voltage regulator ● Easy access front-panel adjustments ● Under-frequency, stability and voltage adjustments ● Internal provisions for automatic voltage build up from generator residual voltage ● Electromagnetic interference filter
Alternator Data Features
Manufacturer Stamford
Type Self-Excited
Insulation NEMA Rise/Temp NEMA H/125°C
Hertz 60
Phase 3
RPM 1800
Leads 12
Amortisseur Windings Full
CFM Cooling Required 286
Voltage Regulator AS480
Sensing Single Phase
Voltage Regulation, No Load - Full Load 1.0%
● BS EN 60034, BS5000, VDE 0530, NEMA MG1-32, IEC34, CSA C22.2-100, and AS1359 complaint ● IP23 enclosure ● Dynamically balanced to exceed BS6861:Part 1 Grade 2.5 vibration standard ● Quality assurance to BS EN ISO 9001 ● Self-ventilated and drip proof construction ● Two-thirds pitch stator and skewed rotor ● Heavy duty bearings ● Fully guarded ● Overexcitation protection ● Under frequency protection ● Overload protection ● Paralleling compatible ● Single-phase sensing
DGC2020 Digital Controller ● Integrated engine-genset control, protection, and metering ● Microprocessor allows for exact measurement, setpoint adjustment, and timing functions ● Front panel 3 position controls and indicators enable quick and simple operation ● Emergency stop push button and an Alarm Horn with silence button ● A wide temperature-range liquid crystal display (LCD) with backlighting ● SAE J1939 Engine ECU communications ● Remote RS-485 communications for Optional RDP-110 Remote Annunciator ● 4 programmable contact inputs and 10 contact outputs (2 ADC rated) ● Modbus Communications with RS-485, Battery Backup for Real Time Clock, UL recognized, CSA certiﬁed, CE approved, HALT (Highly Accelerated Life Tests) tested ● IP 54 Front Panel rating with integrated gasket and NFPA 110 Level 1 Compatible. ● Manual Override Keyswitch Analog Controller with Emergency Bypass Key Switch ● Automatic CANBUS Engine Control ● Oil Pressure, Water Temperature, Battery Voltage and RPM Gauges ● Automatic Gauge Zeroing on Shutdown ● AC Voltage, Frequency, Percent of Load, and Run-Time Metering ● 3-Position Auto-Off-Manual Control Switch ● LED Status Lights: Low Oil Pressure, High Temperature, Overcrank, Overspeed, & Engine Start
standard features and options
Warranty |  |  | ® ● Heavy Duty Steel Base ● Vibration Isolators | [10 empty] | Standard Features: ● Battery Charging Alternator ● Factory Powder Coating
2 Year Standard
5 Year Comprehensive
Controller Options | [6 empty] | ● Oil Drain Valve with Extension ● Battery Rack & Cables ● High Ambient Unit Mounted Radiator | [8 empty] | ● Factory Test ● Owner’s Manual Miscellaneous Options:
DGC-2020HD Controller
Fiber Optic Ethernet (DGC-2020HD)
RS-232 Port & Generator Protection (DGC-2020)
Flush or Surface Mount Remote Annunciator
Remote Mount Break Glass E-Stop Switch
● Battery Charger ● Coolant Drain Kit ● Block Heater ● Line Circuit Breaker | [16 empty] | ● Pad Type Battery Heater ● Battery Heater Blanket w/Thermostat ● Oil Pan Heater ● Generator Strip Heater
Narrow Skid Base Open Unit Options: ● Radiator Duct Flange ● Flex Exhaust ● Critical Silencer ● Wide Skid Base OVERALL SIZE: 60”L x 26”W x 53”H Approximate Weight: 900 lbs. Note: Dimensions and weights reﬂect standard open unit with no options and are subject to change. Standard Enclosed Unit Options: ● Sound Attenuated Enclosure ● Load Center, Lights & GFI Receptacle ● Sub-Base Fuel Tank OVERALL SIZE: 78”L x 46”W x 46”H Approximate Weight: 1,200 lbs. Note: Dimensions and weights reﬂect standard enclosed unit with no options and are subject to change.
Note: The above drawings are provided for reference only and should not be used for planning installation. Contact your local distributor for more information. | [19 empty] | 12/18